DIESEL MOTOR

GENERTATOR

FUEL ACTUATOR

FUEL PUMP

GOVERNOR

CRANK

SPEED CONTROL

LOAD SHARE

DROP LINE

CROSS CURRENT

AVR 400Hz

AVR 50Hz

LOAD SHARE

DROP LINE

CROSS CURRENT

V MTR

A MTR

KW MTR

V MTR

A MTR

KW MTR

SYNCHRONIZE

TO GEN 2

BATTERY CHARGER

Hz MTR

Το κύκλωμα της γεννήτριας αποτελείται από τρία υποσυστήματα .

Το ένα ελέγχει τα μηχανικά μέρη της γεννήτριας ένα άλλο τα ηλεκτρονικά ένα τρίτο τα ηλεκτρικά

Στα μηχανικά μέρη περιλαμβάνονται

ο έλεγχος του μοτέρ εκκίνησης (μίζα).

φόρτιση της μπαταρίας

παροχή καυσίμου

τάση τροφοδοσίας των αντιστάσεων αποφυγή υγροποίησης.

Ενδείξεις και προστασίες για υπερθέρμανση .

Ενδείξεις και προστασίες για φίλτρα αέρος

Κυκλώματα προστασίας του κινητήρα

Στα ηλεκτρονικά περιλαμβάνονται

Ο έλεγχος τάσης

Έλεγχος παραλληλισμού ρεύματος

Έλεγχος συγχρονισμού φάσης

Έλεγχος ισχύος

Κυκλώματα προστασίας της γεννήτριας

Στα ηλεκτρικά περιλαμβάνονται

Ενδεικτες τάσης , ρεύματος , ισχύος

Διακόπτες μικτονομισης

Κυκλώματα προστασίας ηλεκτρικών.

Γενικά δεν θα πρέπει για οποιοδήποτε ενέργεια από τον χειριστή να δημιουργείται βλάβη η πρόβλημα στην καλή λειτουργία του όλου συστήματος.

ΜΗΧΑΝΙΚΑ

Ο έλεγχος του μοτέρ εκκίνησης (μίζα).

Παρέχει βασικούς ελέγχους προστασίας από παρατεταμένη χρήση του μοτέρ,

Την αποφυγή χειρισμού κατά το διάστημα που η μηχανή λειτουργεί

Η φόρτιση της μπαταρίας

Κύκλωμα φόρτισης από εξωτερική πηγή όταν η μηχανή δεν λειτουργεί (παροχή ρεύματος για αποφυγή υγροποίησης )

Κύκλωμα φόρτισης όταν η μηχανή λειτουργεί

διακοπή φόρτισης κατά το διάστημα που γίνεται εκκίνηση της μηχανής.

παροχή καυσίμου

Ενεργοποίηση βαλβίδας παροχής

Ρύθμιση καύσιμου για λειτουργία ρελαντί

αντιστάσεις αποφυγή υγροποίησης

ρελαι και εξωτερική πηγή τάσης που ενεργοποιούν τις αντιστάσεις κατά το διάστημα που η μηχανή είναι σβηστή , το ίδιο κύκλωμα τροφοδοτεί και την φόρτιση της μπαταρίας.

Ενδείξεις και προστασίες για υπερθέρμανση

Παρέχουν όλες τις ενδείξεις που διαθέτει η μηχανή και έχει οπτικό και ακουστικό συναγερμό

Ενδείξεις και προστασίες για φίλτρα αέρος

Παρέχει ενδείξεις για την ανάγκη αντικατάστασης του φίλτρου.

Κυκλώματα προστασίας του κινητήρα

Ρολόι χρόνου λειτουργίας μηχανής

Πίεση λαδιού

υπερθέρμανση

ΗΛΕΚΤΡΟΝΙΚΑ

Ο έλεγχος τάσης

Δυνατότητα επιλογής φάσης έλεγχου και τρόπου λειτουργίας

Μόνο R , S  η T η  RS , ST , TR η και RST

Δυνατότητα επιλογής χρόνου απόκρισης διόρθωσης και παραμετροποίηση του.

Ασφαλιστική διάταξη για τα thyristor ισχύος

Ασφαλιστική διάταξη για υπέρταση

Έλεγχος παραλληλισμού ρεύματος

Έλεγχος τρόπου λειτουργίας LINE DROP η CROSS CURRENT

Ασφαλιστική διάταξη για υπερρευμα

Έλεγχος συγχρονισμού φάσης

Ένδειξη και χειρισμός για τον συγχρονισμό

Ασφαλιστική διάταξη για αποφυγή παραλληλισμού χωρίς συγχρονισμό

Ασφαλιστική διάταξη για αποφυγή παραλληλισμού χωρίς ισοδυναμία τάσεων.

Έλεγχος ισχύος

Κύκλωμα καταμερισμού ενέργειας με ασφαλιστική διάταξη για αρνητική η πολύ μικρή ενέργεια

Περιορισμός ισχύος σε προκαθορισμένο μέγεθος

Κυκλώματα προστασίας της γεννήτριας

Ένδειξη για Υπερθέρμανση γεννήτριας

Ασφάλειες για υπερρευματα στα διάφορα μέρη που αποτελούν το κύκλωμα.

ΗΛΕΚΤΡΙΚΑ

Γενική ασφάλεια παροχής ρεύματος

Γενική ασφάλεια παροχής ισχύος

Ενδειξεις VOLT AMPERE KWATT Hz ενδεικτικες λυχνιες κλπ

GAC ADC100

The ADC100 Series Integral Actuator is designed to mount directly to Stanadyne D Series fuel injection pumps. When the ADC100 electric actuator is installed on the fuel pump, an integral high performance fuel control system results. No external linkages or brackets are required and no extra Stanadyne parts are needed. In addition, when the governor system is de-energised, the ADC100 Series electric actuator provides the function of a fuel shut off valve.

## ESD5330

A high specification electronic governor speed controller with a high power actuator output capable of controlling the ACB2000 actuator. Includes speed ramping circuitry and starting fuel limiting for engine emission control, a two element speed switch as well as all the features of the ESD5100 series.

## ACB2000

The ACB2000 actuator is a rotary output, linear torque proportional electric servo designed for electro-mechanical actuation of fuel system control levers requiring torques in the 5 lb-ft (6.7 N-m) range. The actuator is energised by appropriate speed control unit signals, and is capable of 35 degrees of rotation with torques as high as 12 lb-ft (16.2 N-m). Suitable for engines from 800 - 1800hp (600 - 1340kw).

### EAM108

To interface GAC load sharing and synchronising units to Woodward 8290-038 electronic governing speed controller.

### SSW676

The SSW676 is identical to the SSW675 with the addition of a third speed switch element for intermediate speed sensing such as under speed etc

## SYC6714

The SYC6714 automatic synchroniser adjusts the engine speed via the electronic governor speed controller to obtain an equal phase relationship between the oncoming generator and the secondary power source. A built in 'synch check' function is provided and the unit activates an internal relay to signal the generator circuit breaker/switch to close. The SYC6714 is very simple to set up, has adjustable Gain, Stability and Breaker Closure Phase Angle Window and provides indication of when it is enabled, when the power sources are synchronised and when the Breaker Closure relay is energised. The SYC6714 automatic synchroniser can be used with GAC EAM Interface Units to synchronise engines with non-GAC electronic governor speed controllers.

## VMA100

The GAC VMA100 is designed to sense line to neutral ac voltages of a generator set and the mains and will adjust the generator voltage to match the two terminal voltages. Raise and lower relay contacts within the VMA100 can either operate a motorised potentiometer or be connected directly to an alternator automatic voltage regulator with digital raise/lower inputs. The AC voltage can be matched to a tolerance band of 0.5%,1% or 2.5% of centre. The VAM100 can be connected to the SYC6714 to provide a breaker closure inhibit signal to ensure voltage matching is achieved before closing the generator breaker.

## LSM201

A multi-function isochronously load share unit with all the functions of the LSM 672 plus new enhanced load/power control technology. Adjustable time delays for forward and reverse power monitors, automatic adjustable power ramping function for soft loading and unloading of individual sets in parallel, generator power ramping to the mains with adjustable ramp time constants, complex import/export and peak load sharing control and internal power metering and reverse power protection. The load share unit also has a facility to supply an external power meter with a -1 to + 5 volt signal that is proportional to CT currents (The -1 volt indicates reverse power). Available in 12 and 24-volt versions.